## Pol01 Calculator
BREEAM International 2016 Pol 01 Impact of refrigerants calculator
System Type/Name | R-Number | Refrigerant charge (kg per kiwi coolth capacity) | System capacity (kW) | Total refrigerant charge (kg) | System operational life (yr) | Refrigerant Global Warming Potential | Annual leakage rate (% refrigerant charge) | Annual purge release factor (% refrigerant charge) | Annual service release (% refrigerant charge) | Probability factor for catastrophic failure (%) | Refrigerant Recovery efficiency (%) | Refrigerant loss (operational) | Refrigerant loss (retirement) | Total lifetime refrigerant loss (kg) | CO2 equivalent (kg) | Direct Emissions Life Cycle kgCO2equiv/kW coolth capacity
VP1-4 | R134a |  | 120000 | 80930 | 10 | 1430 | 1.001% | 0% | 0.1% | 0% | 98% | 8909.3 | 1618.6 | 10527.9 | 15054897 | 125.4575 | 1 | 0
VKA1-2 | R134a |  | 10000 | 2562 | 10 | 1430 | 1.97% | 0% | 0% | 0% | 98% | 504.768 | 51.24 | 556.008 | 795091.3818 | 79.5091 | 1 | 0
VKA11-15 | R134a |  | 12500 | 2614 | 10 | 1430 | 0% | 0% | 0% | 0% | 98% | 0 | 52.28 | 52.28 | 74760.4 | 5.9808 | 1 | 0
VKA21-22 | R134a |  | 12000 | 2870 | 10 | 1430 | 5.131% | 0% | 0% | 0% | 98% | 1472.7273 | 57.4 | 1530.1273 | 2188082 | 182.3402 | 1 | 0
Frikyla | Vatten |  | 15000 | 0 | 10 | 0 | 0% | 0% | 0% | 0% | 98% | 0 | 0 | 0 | 0 | 0 | 0 | 0
VP5-9 | R1234ze |  | 7500 | 1400 | 10 | 7 | 0% | 0% | 0% | 1% | 98% | 140 | 28 | 168 | 1176 | 0.1568 | 0 | 0
Fjärrkylanläggning | Vatten |  | 20000 | 0 | 10 | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  | 0 | 1
[12 empty] | 0 | 0 | 0 | 0 |  | 0 | 1
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  | 0 | 1
|  |  | 197000 | [11 empty] | 18114006.7818 | 91.9493 | 4 | 3
Total system cooling/heating capacity | 197000 |  | kW
Total Direct Effect Life Cycle CO2e emissions (DELC) | 91.9493 |  | kgCO2e/kW coolth capacity
Total Pol 01 credits achieved | 2
Note on G5: Where system specific data are not available use default values in table 54.
Note on I5: Where system specific data are not available use default data in table 55.
Note on J5: Where system specific data are not available use default factor 5%. If the system does not require an annual purge, zero should be used.
Note on K5: Where system specific data are not available use default factor 0.25.
Note on L5: Where system specific data are not available use default factor 1%.
Note on M5: Where system specific data are not available use default factor 95%.

## Schedule of changes
BREEAM International 2016 Pol 01 Impact of refrigerants calculator
Current Version | Release date | Description of changes/additions to previous version resulting in current version
1.1 | 2017-10-04 | New rows added
Previous Versions | Release date | Description of changes/additions
1 | 2016-03-21 | BREEAM 2016 New Construction go live version